(Specifier Note:  The purpose of this guide specification is to assist the specifier in correctly specifying a battery monitoring system and its installation.  The specifier needs to edit the guide specifications to fit the needs of specific projects.  Contact a Cellwatch Product Representative to assist in appropriate product selections.  Throughout the guide specification, there are Specifier Notes to assist in the editing of the file.

References have been made within the text of the specification to the current Master Format Section numbers and titles; specifier needs to coordinate these numbers and titles with sections included for the specific project.  Brackets [ ] have been used to indicate when a selection is required.  Specifier Notes should be deleted after editing has been completed.

SECTION 26 33 46

BATTERY MONITORING

- NDSL, Inc. - Cellwatch

- Battery Monitoring System

GENERAL

SECTION INCLUDES

A daily monitoring system for lead acid and nickel cadmium batteries used as back-up power.  Daily battery monitoring system consists of a means for monitoring battery voltages, Ohmic value, temperature and current.  Custom wiring harnesses shall not be used and no load greater than 4 amps shall be used for measuring Ohmic values.

Windows embedded software, hardware, cabling and associated accessories shall be included with the system.

- (Specifier Note:  The CSI Construction Specifications Practice Guide recommends the inclusion of the date of the reference standard.  In lieu of the inclusion of the date herein, the specifier may include the following statement in Division 01, Section 01 42 00 – References:  “The date of the standard is that in effect as of the date of receipt of bids for the project.”)

REFERENCES

Reference Standards:

Conformance European (CE): EMC

Emissions:	EN61326-1:2007, FCC Part 15B and ICES-00

Immunity: 	EN61326-1:2006

Canadian Standards Association (CSA)

Safety: 	CAN/CSA C22.2 NO. 61010-1-12

Safety:	CAN/CSA C22.2 NO. 61010-2-030-12

Underwriters Laboratory (UL): Safety

Safety:	UL 61010-1:2012

Safety:	UL 61010-2-030:2012

International Organization for Standardization (ISO)

ISO 9001:  Quality management systems – Requirements for quality of manufactured goods.

National Electric Code (NEC)

National Fire Protection Association (NFPA):

NFPA 70:  National Electric Code.

cTUVus

Definitions:

Battery:  A DC electrical storage system consisting of cells or containers connected in series to achieve the required DC voltage.  Strings are connected in parallel to achieve the required back up time.

String:  A sub-division of a battery.  A group of cells or containers connected in series.

Container:  A housing which contains multiple cells.

Cell:  The basic unit of a container, traditionally consisting of lead acid or nickel-cadmium and delivers a nominal 1.2 to 2 VDC.

Pilot Cell: One container of a string selected to obtain temperature readings.

ADMINISTRATIVE REQUIREMENTS

Pre-installation meeting:  Conduct a pre-installation meeting at the job site attended by Owner, [Architect] [Engineer], manufacturer’s technical representative, installer, and contractors of related trades.  Coordinate installation, and other requirements specific to the project.

SUBMITTALS

- (Specifier Note: DELETE Submittal Procedures paragraph when not required. Coordinate requirements with Division 01, Section 01 33 00 – Submittal Procedures.)

Refer to Section [01 33 00 Submittal Procedures] [insert section number and title].

Product Data: Submit manufacturer current technical literature for each type of product.

Shop Drawings; Submit detailed drawings showing:

Assembly details of standard components.  Indicate necessary dimensions, arrangement of components, clearances and access requirements.

Include detailed wiring diagrams for power and control wiring.

Delegated-Design Submittal:  For battery monitoring system indicated to comply with performance criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Quality Assurance Submittals

- (Specifier Note:  DELETE Design Data, Test Report submittal requirements when a proprietary specification is used.  MAINTAIN Design Data, Test Report submittal requirement when other products may be submitted as substitutions.)

Manufacturer Installation Instructions:  Provide manufacturer’s written installation instructions including proper material storage, and maintenance instructions.

- (Specifier Note:  DELETE warranty submittal if proprietary specification is written using only Cellwatch System.)

Submit copy of manufacturer’s warranty.

QUALITY ASSURANCE

Manufacturer Qualifications:

Manufacturer shall have comparable Battery Monitoring Systems (BMS) in operational service a minimum of ten (10) years.

Manufacturer shall be registered and certified by ISO 9001.

Manufacturer shall have a minimum of 2 sources for all major manufactured components, both shall be ISO 9001 registered and certified.

Upgrades to the system shall have backward compatibility so that major components are not required to be replaced.

Repair process is facilitated by component replacement and should not require returning the system to the manufacturer.

Installer Qualifications:

Installer shall be authorized, trained, and certified to install BMS by the manufacturer.

DELIVERY, STORAGE AND HANDLING

- (Specifier Note: DELETE Product Requirement paragraph when not required. Coordinate requirements with Division 01, Section 01 60 00 – Product Requirements.)

Refer to Section [01 60 00 Product Requirements] [insert section number and title].

Deliver materials and components in manufacturer’s original, unopened, undamaged packaging with identification labels intact.

Store materials on dry, level, firm, and clean surface.

WARRANTY

Refer to Section [01 78 00 Closeout Submittals] [insert section number and title].

Warranty:

Standard form in which manufacturer agrees to repair or replace products that are defective in materials or workmanship within the specified warranty period.

Warranty Period: One (1) year from date product is placed in service, or 15 months for date of shipment from manufacturer, whichever occurs first.

Endemic Warranty:

Endemic Warranty shall be defined as follows:

Greater than 4 failures or 10 percent failure rate, whichever is greater, of any piece of warranted equipment on any one location in any one 12-month period.

10 percent failure rate of any single piece of warranted equipment in the field population.

When an endemic warranty condition occurs, the installer will assist the end-user in one of the following forms:

Pay the end-user reasonable labor costs to remedy or attempt to remedy the endemic warranty condition.

Provide staff, travel and accommodation to remedy the endemic warranty condition.

During the endemic warranty condition remedy if it is discovered that the cause was not attributable to defective manufacturer’s materials or workmanship the end-user shall reimburse manufacturer for costs incurred.

PRODUCTS

- (Specifier Note: Product Information is proprietary to NDSL’s “Cellwatch Battery Monitoring System”. If additional products are required for competitive procurement, contact NDSL, Inc. for assistance.)

MANUFACTURER

NDSL Inc.; Raleigh, NC 27612 919-790-7877 (www.cellwatch.com)

Basis of Design:

“Cellwatch Battery Monitoring System”

- (Specifier Note: DELETE or COORDINATE Substitution Limitations paragraph if substitutions are addressed in Division 01, Section 01 21 00 – Substitution Procedures.)

Substitution Limitations:

Submit written request for approval of substitutions to the [Architect] [Engineer] [a minimum of [14] days prior to the date for receipt of bids] [Insert bid date].  Include the following information:

Name of the materials and description of the proposed substitute

Drawings, cut sheets, performance

List of projects of similar scope

Other information necessary for evaluation

List of all exceptions and Deviations to this Specification

After evaluation by [Architect] [Engineer], if approved, approval will be issued via addendum. No verbal approval will be given.

Substitutions following award of contract are not allowed except as stipulated in Division 01 – General Requirements.

PERFORMANCE CRITERIA

Delegated Design: Design battery monitoring system by a qualified professional engineer, using performance criteria indicated.

Battery Monitoring System (BMS):

Provide transient voltage surge suppression for system components.

Battery types monitored by semi-permanent connection to battery system:

Valve regulated lead acid (VRLA) Sealed batteries: Ohmic value range 1 to 50.0 mΩ

Flooded cells or Value Regulated lead acid 2v VRLA:  Ohmic value range 0 to 6 mΩ

Ni-CAD batteries: Ohmic value range of 0 to 6 mΩ

Components shall have the following regulatory approvals:

CE listings for electrical noise emissions and susceptibility.

- Emissions: EN61326-1:2007, FCC Part 15B and ICES-00

- Immunity: 	EN61326-1:2006

The following listings are for electrical safety:

- CAN/CSA C22.2 No. 61010-1-12

- CAN/CSA C22.2 No. 61010-2-030-12

- UL 61010-12:2012

- UL 61010-2-030:2012

System Capacity:

Potential Voltage value measurement points:  1 to 30,000

Potential Ohmic value measurement points:  1 to 30,000

(Optional) Potential Cell Temperature value measurement points: 1 to 30,000

AC Ripple Voltage measurement points: 1 to 124

DC String Float Voltage measurement points: 1 to 124

Supports different voltage cells from 1.2vdc to 2vdc (low voltage containers) and 4vdc to 16vdc (high voltage containers) on the same system

Current Sensors:  1 to 124

Ambient or Pilot Cell Temperature Sensors:  1 to 124

Integrated Battery Monitoring Unit (iBMU) – Component capacity: 31 Control Units (CU)

Control Unit (CU) – Component capacity:

254 Data Collection Modules (DCMs)

4 current measurement inputs

4 temperature measurement inputs

4 volt-free relay contact for external alarms

Visual indicator for Powered On / Communications Active Thermal Runaway Controller

The system meets thermal runaway requirements defined in IFC 1206.2 (Formerly IFC 608.3) and NFPA 855.9.3

Four relays will be incorporated to disconnect each string.  Relays will be rated up to 30vdc or 250vac at 5amps.

Visual indicators will be used on each Control Unit to indicate when a string is in Thermal Runaway.

Measurement ranges:

Module Point Voltages:  1.2v DC to 4v DC nominal or 4v DC nominal to 16v DC nominal

Temperature measurement:  2°C to 80°C | 36°F to 176°F

Point temperature measurement for negative terminal temperature monitoring: 2°C to 80°C | 36°F to 176°F

Ohmic value range:  0 to 6,000µΩ for single-cell containers or 1 to 50,000 µΩ for multi-cell containers.

Current measurement:  Scalable 10 to 5000 amps depending on number of conductors used

The system shall not require any calibration at installation, yearly intervals or when containers are replaced.

The Battery Monitoring Systems shall be modular.  Components of the BMS shall be reconfigurable to allow for changes in battery layouts and shall have the ability to add or remove BMS components without changing the entire system.  New components or revisions shall be backward compatible.

Software:

System shall operate using Windows embedded operating system and shall be capable of loading operating system and initialize scanning without user intervention.

Monitoring capabilities:

Monitored Data:  Provide for each [Cell] [Container] [or] [String where indicated], in the Battery Monitoring System.  Each operation listed shall be capable of being programmed with upper and lower alarm operating limits.

Voltage.  (The BMS shall be able to support different voltage cells on the same system)

Ohmic value (including inter-cell link resistance). (System should not damage the battery or have a measurable impact on the battery due to ohmic value measurement)

Charge/Discharge current

Pilot cell temperature  Individual container temperatures

Ambient temperature

Ripple Voltage

Thermal Runaway conditions

Alarm Conditions: program shall be capable of indicating the following either by [visual alarm indicator] [or] [audible alarm]:

(Specifier Note: Ripple Voltage measurement can be selected as an option or removed if not required)The system shall be configurable for monitored data that exceeds predetermined or programmed limits set for the entire system, or by battery, string or individual cells or containers.

Cell or Container Voltage

String Voltage

Ripple Voltage

Ohmic Value

Current

Temperature

Current Discharge Event:  Occurs when the current outflow exceeds the predetermined and programmed limits set.

Current Recharge Event:  Occurs when the current inflow exceeds the predetermined and programmed limits set.

The system shall provide five or more volts free alarm relays to permit interface to third party devices.

Ohmic value should be automatically and uniquely programmable for each container/cell for the entire system or per string.  The system should also automatically revise the base line ohmic value alarms after 35 days following the date of the monitoring system commissioning.

- Specifier Note: If Thermal Runaway protection is not required this section can be deleted)

Thermal Runaway (optional) shall be able to meet the requirements of IFC 1206.2 (Formerly IFC 608.3) and NFPA 855.9.3 and shall include an audible and visual alarm capabilities including LEDs on the Thermal Runaway Controller, a warning state with programmable delay to isolate the string from the UPS.  The Thermal Runaway condition shall be dependent upon current, temperature of string or container and container voltage.  The BMS shall provide advanced notification so issues can be addressed without putting mission critical loads at risk.

E-mail Alert Alarm Notification.  The BMS shall have the ability to send an e-mail when an alarm occurs.  Each e-mail send will include details about the site location, battery, string, date, time and type of alarm event: voltage, ohmic value, current, temperature, thermal runaway or discharge.

Monitoring frequency:  The customer shall have the ability to set the frequency of data collection for voltage and ohmic value.  Voltage data shall be able to be logged constantly, every hour or every 6 hours.  Ohmic value shall be logged every 12 or 24 hours.

Continuously measure the following at an interval of more than once per minute:

Charge current

Discharge current

Pilot container temperature

Ambient temperature

Individual container temperature

Individual container voltage during discharge

String voltage during a discharge

Ripple voltage

- (Specifier Note: Float voltage measurement shall be set between 4 and 24 times each day.)

Float voltage measurement:  Measurement set between [4] [24] times each day

Ohmic measurement:  Measurement set to [1] or [2] time[s] each day

Monitored Data and Analysis:  All retrieved data shall be stored and may be displayed as a spreadsheet in most formats (e.g. Microsoft Excel). The system shall have the ability to store at least 10 years of historical data on the iBMU. All measurement records can be extracted to a CSV file for easy viewing.

Daily Archival:

Monitored data shall be captured daily.

A trend analysis of monitored data shall be provided.

Ability to display archived data and trend analysis.

Analysis Graphs:  Displayed as line or bar charts, except trend analysis and discharge graphs which shall be displayed as line graphs.

Each cell or container monitored data for the current day

Each cell or container monitored data for the complete history stored

Most recent voltage and ohmic reading for each string

A trend analysis of monitored data for each year of operation

An analysis of the best and worst performing Cells, Containers or Strings in a system discharge.  Provide the capability of adding all Cells, Containers in the system

Alarm condition – Current outflow event:  Discharge analysis showing all battery voltage curves for performance analysis.  Graph shall be able to show one to all cells or containers in the system. Analysis graphs shall be capable of allowing user defined colors.

Analysis graphs shall be printable, each graph individually or all graphs.

Graphs of historic data should provide support for panning and zooming.

Graphing tool should support overlay of alarm setting for each cell or container as an overlay to the actual measurement.

Graphs should provide support for dual axis plotting of measured parameters in a single graphic view.

The system shall support Modbus TCP/IP and SNMP interfaces.

The system shall incorporate a separate program to manage alarm data.  It shall include the ability to sort events by type, alarm value, time and start or end date.  All reports can be generated and exported to a CSV file.  All active alarms shall be shown in red, acknowledged alarms shall be denoted with a check mark.   Users must be able to filter alarm events by using the battery, string or cell/probe selections.  As an option the user can select only batteries, strings and cells/probes that have alarmed will be available for filtering.

The system shall be able to provide reports for:

Total String/Battery Float Voltage

Individual Container/Cell Float Voltage

Discharge Voltage per Container/Cell

String Current

Ambient Temperature

Pilot Temperature

- Specifier Note: Per Cell Temperature, Ripple Voltage and Thermal Runaway are options and may be deleted if not required)

Per Cell Temperature

Ripple Voltage

Thermal Runaway Conditions

Dependent upon Current, String Temperature and Container Voltage

The system shall be able to physically identify cells or containers under investigation via a ping feature which will cause an audible alarm and flash an LED at the DCM(s) indicating which container(s) under investigation.

- Specifier Note: Real-Time Centralized Reporting and Accessibility is optional and may be deleted if not required)

Real-Time Centralized Reporting and Accessibility should be supported by the system.  The centralized server should provide a graphical user interface compatible with the same browsers supported by the battery monitoring system.  The system will provide real-time information about the state of the batteries monitored by communicating directly with each iBMU system.  Data should be visible in both graphical and numerical format and alarm states should be displayed based on the site, system, battery, string and, if applicable, container that is in alarm.  The data should be accessible through a multi-privilege level, password protected user interface hosted on the customer network.  The system should allow users the ability to download, backup, and provides a means of viewing battery data, including historical, discharge, and recharge data. The system shall be able enable or disable remote real-time metric reporting capabilities to a centralized system located on the customer network.  The local system should have the ability to enable or disable communications with the centralized server.  The local system shall also be able to enable or disable permissions for the remote system to initiate system scans or modify system controls.  Multiple levels of user access are required to allow an administrator to select whether the user can view the system or view the system and control the commands.

COMPONENTS

Integrated Battery Monitoring Unit (iBMU):  The iBMU will control all aspects of the monitoring process including retrieving, displaying and saving data; indicating alarm activation; processing data for historical trending; real time calculations; and control outputs to trigger external functions.  The data will be presented on a customer supplied and connected color screen or over an Ethernet network connection via MODBUS over TCP/IP, SNMP, via an integrated webpage, using Remote Desktop, or a customer supplied and connected KVM over IP. A KVM over IP option allows the iBMU to be accessible via the network but isolated from the network as the KVM connects directly to the Video, Monitor, and Mouse ports on the iBMU.  The iBMU should support real-time control and reporting to a centralized system for advanced data analysis that can be enabled or disabled.

Mounting: [Wall] [Rack] mounted.

iBMU hardware – minimum requirements:

1.6Ghz processor

8GB RAM

120 GB Solid State Hard drive+

Windows 10 LTSB

Fan-less Mother Board

2 Network Interface Connector (NIC) 10/100/1000 Mbps/s Ethernet Connections

One static service port (192.168.0.128/255.255.255.0)

One dynamic (DHCP enabled)

1 VGA Video Port, 1 HDMI Port

1 RS 485 Port for connections to the Control Unit(s)

6 USB Ports

Communicates with up to 31 Control Units

Power: [110] [240] VAC, 300 Watts, Redundant input optional

Component connections:  RS485 cable, Belden 8102 or 88102

Language: [English] [French] [Mandarin] [Korean] [Japanese]

Standard connections for external components:

Ports: Printer, [1 USB port]

Modem:  external USB Modem device

2 USB ports

2 Network Interface Connector:  10/100Mhz Ethernet connection

Control Unit (CU):  The Control Unit shall communicate to the DCMs via a fiber optic loop. The functions of the Controller include; conversion between digital RS485 and optical signals, up to four independent current readings per Control Unit, up to four independent temperature reading per Control Unit for ambient and/or pilot cell temperatures and the facility for five volt free contacts to be used as alarm and control outputs.  For units requiring thermal runaway protection the control unit must have 10 volt free contacts to be used for alarm and control outputs. Addressing should be able to support a total of 31 RS-485 Addresses connected to a single IBMU.  The Control Unit must support a dedicated 485 communications interface up to 2000’ from the iBMU.

Mounting:  Wall mounted

Power: [110] [240] VAC, 20 Watts, must be powered from a UPS backed supply

CU hardware – minimum requirements:

Controls 254 Data Collection Modules (DCMs)

Includes 4 current inputs.

4 temperature probe inputs.

4 alarm triggered volt free relay contacts and 1 communications failure triggered volt free relay contact

10 alarm triggered volt free relays for Thermal Runaway Controller

Interface for generator or ancillary battery monitoring extension via RJ45 connector

Sensing inputs:

Temperature- Solid state probe

Resolution- 0.05 degrees C

Accuracy- +/- 1 degree C

Range- 2 to 80 degrees C

Current- Solid state magnetic core sprung clamp 2” (50mm) capacity 1,000 amps or 4.5” (112mm) 2,500 amps

Resolution- 1.0 amps

Useful Range- +/- 10 to maximum amps of clamp

Component connection:  RS485 cable, Belden 8102 or 88102.  Sensing cable, Belden 8723SB

Generator Kit: The system shall be capable of monitoring small remote batteries typically used for generators up to 4000ft from the BMS

Modules used for monitoring generator batteries should be capable of being installed in parallel with the DC charger and capable of monitoring 2 to 4 cells or containers per remote string.

Data Collection Module (DCM):  Data collection modules shall measure voltage and Ohmic Value for of up to four measurement points to which they are connected. All electrical wiring shall be affixed to the DCM prior to shipment and no cable crimps shall be required during installation. DCMs shall have an option for measuring the temperature on the negative post of each container.   DCM shall utilize fiber optic cable for communications to ensure reliability, noise elimination and safety.  Electrical wiring between DCMs is NOT acceptable.  Each DCM shall support a fiber optic transmitter (white or blue connector) and a receiver (black connector) that is fiber cabled to provide a fiber connection between each DCM and continues until a loop is formed returning to the Control Unit.  Maximum distance between DCMs will be up to 150’.  The maximum rating of any DCM is 12VDC (low voltage) or 80VDC (high voltage) standard.

- Specifier Note: DCM VDC measurement rating set to [12] [60] or [80]

Mounting: [Dual Lock] or [DIN Rail]

Conductors shall be minimum 22 and maximum 14 AWG, 300 v rated, 15amp maximum, insulated wire meeting the requirements of UL 1015

Conductors shall be color coded.

All wiring that connects to the battery terminals should be acid resistant.

Each DCM can measure up to 4 containers or cells data.  Data collection includes:

Voltage

Ohmic Value

DCM shall have a sleep mode that after 25 hours of no communication with the Control Unit it shall reduce the power requirement to less than 2ma to conserve battery life.

Average current draw during ohmic testing shall be less than or equal to 0.5 amps for VRLA and 2 amps for VLA and Ni-CAD

Voltage range shall be 0 to 80vdc with 2mv resolution with accuracy of 0.1%, +/-5mv for multi-cell VRLA applications and shall be 0 to 12vdc with 2mV resolution with accuracy of 0.1% +/- 5mv for single-cell Ni-Cd and Lead-Acid applications.

Ohmic value range 1 to 50 mΩ with accuracy of 1.5% for 4V-16V VRLAs and 0 to 6 mΩ with accuracy of 2% +/-4 µΩ for 1.2V-2V VRLAs, VLAs and Ni-CADs

Ripple voltage (40 Hz to 1K Hz) range 0 to 5 VAC rms with resolution of 1 mV rms and an accuracy of 2% +/- 5mV

- Specifier Note: Temperature is required for thermal runaway protection on open stack, open rack, VRLA and VLA systems.

Temperature range shall be 2C to 80C monitored at the negative post with +/- 1C accuracy.

Component connection:

Factory installed terminators on 40-inch wire harness to Containers.

Fiber optic cable for data communication between DCMs and the CU.

DCM units connected to generator batteries must be able to provide consistent reliable readings when monitoring two or more containers in series while also connected in parallel with a DCM charger or in parallel with another battery string.

The DCM unit shall also continue to operator without interruption when the battery voltage drops during the initial surge from the generator starting sequence.

- Central Management System (CMS):  Specifier Note: Hardware is only required if the user does not utilize a virtual machine or existing server

- The CMS should be able to be operated on a customer run VM Ware system, Windows OS, or dedicated hardware meeting minimum requirements.  For the dedicated hardware option, the following requirements apply:

Mounting: [Wall] [Rack] mounted

CMS hardware – minimum requirements:

Dual Core or higher 1.5 GHz+ processor

512 MB ram or higher

250 GB Hard drive or higher

1 Network Interface Connector: 10/100/1000 Mbps/s Ethernet Connection

Windows OS (10 or higher)

Power: [110] [240] VAC, 300 Watts, must be powered from a UPS backed supply

Language: [English] [French] [Mandarin] [Korean] [Japanese]

Standard connections for external components:

Ports: 1 USB port minimum

Modem:  external USB Modem device

2 USB ports

2 Network Interface Connector:  10/100Mhz Ethernet connection

ACCESSORIES

DCM Cables Specifications:

- Fiber optic cable shall be acrylic, 1.0mm core diameter and 2.2mm outside diameter with a 400-700 nm wavelength.  The supplied fiber optic cable must be acid resistant, highly isolated, and immune to electrical noise.

Current Transducers (CT):

Mounting:  Battery lead, clamped around one or more bus conductor(s)

Component connections: Standard 35’ cable provided by manufacturer.  Maximum distance is 150’.

Solid state, magnetic core sprung clamp. 2” (50mm) capacity, 1,000 amp or 4.5’ (112mm) 2,500 amp.

Temperature Probe (TP):

Mounting: bolted via 8mm (5/16”) lug fitted or with removable adhesive pad

Component connections: Standard 35’ cable provided by manufacturer.  Maximum distance is 150’.

Solid state probe

Isolated up to 1500 V to protect the BMS hardware and battery

- (Specifier Note: If external annunciators, such as buzzers, light fixtures, etc., are provided under another section indicate section number and name.  Delete if no annunciators are required.)

[External Annunciators:  Refer to Section [Insert section number and name]]

EXECUTION

EXAMINATION

Equipment: Install to facilitate service, maintenance, and repair or replacement of components of electrical equipment. Connect in such a way as to facilitate future disconnecting with minimum interference with other components.

Verify that power source for all equipment has surge protection as required by manufacturer.

PREPARATION

Coordinate external enunciator’s location and connection to BMS.

Conduit installation:

Listing and Labeling: Metal conduits, tubing, and fittings shall be listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Electrical Contractor to install conduit and provide 120VAC circuit with duplex outlet from the UPS output to provide power to the iBMU.

Electrical Contractor to install conduit and provide 120VAC circuit with simplex outlet from the UPS output to provide power to the Control Units and Thermal Runaway Controllers.

Electrical Contractor to add a network drop and coordinate with end user for provisioning an IP address.

INSTALLATION

General:

Installation shall maintain System TUV listing.

Mount components plumb and rigid without distortion of component chassis.

Ground equipment in accordance with manufacturer’s requirements.

Install and wire components in accordance with the NEC.

No custom wiring harnesses shall be required.

The length of free conductors at outlets for devices shall meet provisions of NFPA 70, Chapter 3.

Install components in locations within the manufacturer’s installation guidelines.

CONFIGURATION and START UP

Factory Authorized service representative must program the system utilizing the end user’s designations for the system components.

FIELD QUALITY CONTROL

Testing Agency: Engage a qualified testing agency to evaluate BMS and perform tests and inspections.

Perform the following tests and inspections with factory authorized service representative:

Operational Test: After installing components, and after electrical circuitry has been energized, start system to confirm proper operation.

Test and adjust controls and alarms limits in accordance with manufacturer’s recommendations.

DEMONSTRATION AND TRAINING

Refer to Section [01 79 00 – Demonstration and Training] [Insert Section number].

A minimum of 2 hours on site customer training shall be completed by the installer before the system is turned over to the customer.  This training will be performed within 48 hours of the completion of the installation.

Engage a factory authorized service representative to train Owner's personnel to adjust, operate, and maintain components.

Completion of manufacturer provided Commissioning report and submission of completed report to the manufacturer for validation.

END OF SECTION